## 020103020011
JPS Specifications Requirement |  | Supplier Response | Supporting Documentation Provided (Yes or No) | Location in Supporting Document. | COMMENTS
Description | STREETLIGHT, LED, 108W, FOR LIGHTING COLLECTOR ROADWAYS, JPS SPECIFICATION # : LED 0507-S-12
Quantity (EACH) | 1000 |  |  |  |  | Yes
Stock Number | 20103020011 |  |  |  |  | No
Manufacturer
Country Of Origin
Unit Cost (USD)
Total Cost (USD) |  | 0
INCO Terms | CIF Kingston Port
Lead Time | 4-6 Weeks
Standards
ANSI/IES RP-8 American Standards for Roadway Lighting
ANSI C136.2 Dielectric Withstand and Electrical Immunity Requirements
ANSI C136.3 Luminaire Attachments.
ANSI C136.10 Locking Type Photo-control Devices and Mounting Receptacles – Physical and Electrical Interchangeability and Testing.
ANSIC 136.13 Metal Bracket for Wood Poles
ANSI C136.15 Luminaire Field Identification
ANSI C136.22 Internal Labelling of Luminaires
ANSI C136.31 Luminaire Vibration
ANSI C136.36A Aluminium Lighting
ANSI C136.36B Concrete Lighting
ANSI C136.37 Solid States Light Sources Used in Roadway and Area
ANSI C136.41 Roadway and Lighting Equipment Dimming Control
ANSI C62.41.2 Surges in Low-Voltage AC Power Circuits
Luminaire shall be UL or CSA listed. Certification from other recognized NTRL laboratories may be considered.
B117-11 Standard Practice for Operating Salt Spray (Fog) Apparatus
D523-08 Standard Test Method for Specular Gloss
D1654-08 Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments
Luminaire Performance:
Correlated Colour Temperature, CCT: 4000 ±500K
Colour Rendering Index, CRI: ≥70
LED Lamp Size (W): Low = 58 to 61 Medium = 108 to 111 High = 161 to 163
Maximum Off state power consumption (W): 0.5W
BUG Ratings: Wattage below 61W (B2-U0-G2) Wattage above 108W (B3-U0-G2)
Operating Temperature: 18°C to 50°C
LED L70 (Hrs.): ≥ 100,000
Approximate Weight: not exceeding than 12 kg
Approximate Dimension: not exceeding (620mm*305mm *110mm(L*W*H)
Luminaire Efficacy (lm/W): 95
Warranty: ≥ 10 years
Power Supply/Driver:
Input Voltage Range (VAC): 110 - 245
Voltage Tolerance: ± 5%
Operating Frequency: 50 Hz ± 2%
Power Factor: ≥ 0.9
Driver Output Current Range (Minimum): 280 - 600mA
One to Ten Volt dimming ballast and 7- pin ballast receptacle
Surge protection: 20kV/10KA
Expected Lifetime: 20 years
Construction of Lamp:
Luminaire design shall be cobra head
Luminaire classification shall be of the cut-off type
Luminaire housing shall be single piece die-cast A360 aluminium.
Luminaire shall be designed to provide tool-less entry and the circuitry shall include quick connect/disconnects to allow easy separation and removal of power supply, surge protector, light module, etc.
Luminaire distribution pattern shall be field adjustable without the use of a tool.
Luminaire housing shall be provided with level bubble to facilitate installation.
Luminaire housing shall be powder-coated grey finish. All final paint finishes shall be subjected to 1,000 hours of the ASTM B117 salt spray tests.
The power door shall be painted RAL 1018 yellow and shall have “JPS” engrave into it metal and shall be visible from ground (expected engraved height is 2”).
Luminaire shall be designed to mount on a 2” diameter, schedule 40 Al. pipe.
Luminaire external housing shall have a minimum rating of IP65 as specified in IEC 60529, with the ability to shed water from inside the housing.
Luminaire housing cooling system shall consist of a passive heat sink with no fans, pumps or liquids.
Luminaire shall be designed and constructed with a photo-control seven-pin receptacle, ANSI C136.41; standard locking three-pole, two dimming poles and two poles for external inputs.
The area housing the power supply and LED module shall have a minimum rating of IP66 to protect against the ingress of water and dust.
Luminaire shall be designed with the ability to tilt to +5° with minimum mount increments of 2.5°. (The tilt feature is required as many existing brackets have a down angle that will require the lamp to be adjusted in order to be installed parallel to the roadway.)
Luminaire external housing (power door) shall be labelled with the wattage for easy identification; the digits shall be 2” and black in colour.
Each luminaire shall have a unique serial number affix to the unit.
Lens of the luminaire which protects the optics shall be rated IK09.
All fasteners shall be stainless steel and all polycarbonate components shall be UV stabilized.
A three-pole terminal block capable of accepting #14 to #10 AWG wire shall be mounted to the housing inside the electrical compartment.
All terminals/connection points shall be properly labelled.
Luminaire Testing
Units shall be tested in accordance with ANSI C136 Series and ANSI/IES RP-8
LEDs shall be tested in accordance with the IES LM-80
Independent third party testing in accordance with IES LM-79-08; report shall be submitted at the time of the tender
Independent third party validation of IEC 62262-2002 (IK09); report shall be submitted at the time of tender
Manufacturer shall be ISO 9001 & ISO 17025 Certified and RoHS compliant
The assembly factory shall be ISO 9001 Certified
Certified test reports shall be provided for each batch of streetlights supplied
Manufacturer shall invite the Purchasers Representatives (2) at the manufacturer's expense, to witness the tests. This invitation shall be extended at least two (2) weeks before the commencement of such tests. The cost of this visit shall be shown separately. This condition may be waived at the discretion of the Purchaser
Interoperability
Responders are required to submit proof of the system interoperability and flexibility to coexist with other systems e.g., AMI, Field Force from implementation elsewhere.
Field testing/Evaluation
Sample devices will be installed and must pass the field evaluation (New Supplier of the item must provide 3 sample of the item. Requirement is waved for supplier already providing the item to JPS.)