## 021802009001
Specifications | JPS Requirement |  |  | Supplier Response |  |  | Supporting Documentation Provided (Yes or No) | Location in Supporting Document. | COMMENTS
Description | TRANSFORMER, PAD MOUNTED, 100 KVA, SINGLE PHASE, 24/13.8 GRDY, SINGLE PRIMARY VOLTAGE, OIL IMMERSED, DEAD FRONT, SECONDARY VOLTAGE 240/120 V. JPS SPECIFICATION No. : 6951-S-14. | [8 empty] | Yes
Quantity | 3 | [8 empty] | No
Stock Number | 21802009001
Manufacturer
Country Of Origin
INCO Terms
Lead Time
Warranty | The minimum warranty period shall be 18 months from date of payment or 12 months in service, whichever occurs first. The transformer shall be guaranteed for a minimum of 3 years in normal operating conditions, against any manufacturing defects or design anomalies.
Standards
3.1.2 | Applicable parts of the following standards shall be observed in the design, manufacture, performance and tests:-
| a) | ANSI C57.12.00 Standard General Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers
| b) | ANSI C57.12.22-1989 Requirements for Pad Mounted, Compartmental- Type, Self Cooled, Three Phase Distribution Transformers with High-Voltage Bushings, 2500 kVA and Smaller: High Voltage, 34 500 GrY/1920 Volts and Below; Low Voltage, 480 Volts and Below.
| c) | ANSI C57.12.21-1992 Standard for Transformers – Pad –Mounted, Compartmental- type, Self Cooled, Single Phase Distribution Transformers with High Voltage Bushings; High Voltage 34 500 GrY/19 920 Volta and Below: Low Voltage, 240/120 Volts; 167 kVA and Smaller.
| d) | ANSI C57.12.10 Safety Requirements for transformers 230 kV and below 833/958 through 8333/10417 kVA, single phase and 750/862 through 60,000/80,000/100,000 kVA, three phase Without Load Tap Changing and 3750/4687 through 60,000/80,000/100,000 kVA with load Tap Changing.
| e) | ANSI C57.12.28-1988 Switchgear and Transformers - Pad Mounted Equipment-Enclosure Integrity.
| f) | ANSI C57.12.70 Terminal Markings and Connections for Distribution and Power Transformers.
| g) | ANSI C57.12.80 Standard Terminology for Power and Distribution Transformers.
| h) | ANSI C57.12.90-1993 Test Code for Liquid- Immersed Distribution, Power and Regulating Transformers and Guide for Short Circuit Testing of Distribution and Power Transformers.
| i) | ANSI Z55.1 Seafoam Green finishes for Industrial Apparatus and Equipment.
| j) | ANSI C57.92-1981 Guide for Loading Mineral Oil Immersed Power Transformers up to and including 100 MVA with 55 oC or 65 oC Average Winding Rise.
| k) | ASTM D1816 Test method of dielectric oil
| l) | CSA C50 Insulating oil, electrical for transformers and switches.
| m) | EEMAC B6-1 Insulating mineral oil for new electrical apparatus.
| n) | NEMA TR-1 Transformers, Regulators and Reactors.
| o) | NEMA TR-P9
| p) | Western Underground Standards, WUG 2.13 Rev 4
| q) | ANSI/IEEE 386-1977
| r) | American Welding Standard, AWS D1.1/D1.1 M: 2008
| s) | Ontario Hydro Specification M-104M-85
| t) | EEMAC Standard L16-1
| u) | NETA Inter-National Electrical Testing Association
4.1 Insulation and Impedance Ratings
kVA | 100
Polarity | Subtractive
Bushings | Two (2) fuly insulated primary high voltage bushing (one (1) ot facilitate loop feed arrangement).
Fuse | The transformers shall be manufactured with a two-fuse primary protection system (bayonet fuse and current- limiting fuse), with overload indicating device
Taps | Two (2) 2 1⁄2% primary taps above and below normal voltage. Taps shall be provided for both the primary voltage levels of the dual voltage transformer. |  |  | Number of Taps and Percentage below and above nominal voltage |  | Tap Operatining on both Voltage? (YES/NO)
Primary Voltage (kV) | 24/13.8 KV GRDY
BIL(kV) | 125
Insulation Class (kV) | 15
Secondary Voltage (Volts) | 120/240
BIL (kV) | 30
Insulation Class (kV) | 1.2
Frequency(Hz) | 50
Continuous rated capacity at 65℃ temperature rise | See Material Schedule for Quantities and Sizes
Impedance (Nominal) as per ANSI | 2.5% +/- 7.5% for 25 kVA or less
4.00% +/7.5% for 37.5 kVA - 167kVA
4.2 Losses
SIZE (KVA) | No Load |  | Full Load | No Load |  | Full Load
25 Single Voltage | 72 |  | 157
25 Dual Voltage | 78 |  | 165
37.5 Single Voltage | 95 |  | 280
37.5 Dual Voltage | 118 |  | 338
50 Single Voltage | 130 |  | 350
50 Dual Voltage | 116 |  | 445
100 Single Voltage | 205 |  | 801
100 Dual Voltage | 205 |  | 836
167 Dual Voltage | 303 |  | 1103
LOSSES | Each individual transformer manufactured shall be test for No Load (core) losses at 100% rated voltage,and for Load (copper)losses at 85 degrees Celsius and fulload current.These tests shall be conducted at the nominal tap setting.The test results for each transformer by serial number shall be forwarded to the Purchaser (Buyer)for evaluation purposes. A loss evaluation will be completed to determine the lowest responsible bidder with respect to the overall best interest of JPSCo. JPSCo will evaluate losses based .
4.3 Performance
4.3.7.Temperature Rise | The temperature rise measured by resistance method shall not exceed 65 ℃ at a maximum ambient temperature of 30°C when operating continuous at rated capacity.
4.3.8. Dielectric Strength | The temperature rise measured by resistance methodshall not exceed 65℃ at a maximum ambient temperature of 30C when operating continuous at rated capacity.
4.3.9. Overload Capacity | The transformers shall be able to carry overloads in accordance with requirements of ANSI C57.92,with moderate sacrifice of life expectancy.
4.4. Audible Sound
4.4 Audible Sound | The audible sound level of transfomers when operating at rated voltage,and measured as per ANSI C57.12.90 shall not exceed the stipulated sound levels indicated below
| Transformer Size kVA |  | Audible sound level dB (Max)
| 25 |  | 48
| 37.5 |  | 48
| 50 |  | 48
| 100 |  | 51
| 150 |  | 55
| 167 |  | 55
4.5 Construction
The Transformer shall be mechanically designed to ANSI requirements,unless otherwise specified
4.5.1 Dimensions | The overall dimensions of the transfomer and compartment shall be kept to a minimum. |  |  | Length (mm) | Width (mm) | Height (mm)
4.5.2 Exterior finish | Modestly sculptured corners and round edges are encouraged. The transformer and compartments shall be painted standard Sea foam Green as per CIL/Glidden,Guertin Brothers SP2422 or owner approved equivalent paint. There shall be no plates or exterior stenciling positioned on the outside of the transformer tank or switching compartment except for a small plate or decal showing the name of manufacturer and high voltage warning labels.
4.5.3 Tank Compartment Assembly
4.5.3.1 | Provision for lifting shall be provided and shall be adequately strengthened, sized and arranged on the tank to provide a suitable lift for the completely assembled unit. The transformer base shall be arranged so that the tank bottom does not touch the pad.
4.5.3.2 | The welding shall conform to AWS Standard.Diagonal break marks on large surfaces sharp edges and protruding parts shall be avoided where possible.
4.5.3.3 | The strength of the transformershall be as such to withstand a minimum gauge pressure of 70 kPa without leakage or pemanent distortion of the tank exceeding 0.25%of the diagonal dimension of the surface so affected.
4.5.3.4 | Provision for lifting shall be provided and shall be adequately strengthened,sized and arranged on the tank to provide a suitable lift for the completely assembled unit.The transformer baseshall be arranged so that the tank bottom does not touch the pad.
4.5.3.5 | Furnished with side mounted parking stand,the parking stand shall be between the two(2)High Voltage bushings. The parking stand shall have sufficient space around it to accommodate Elastimold Cat.#163FTR or equivalent feed- thrust.Bushing spacing shall meet the minimum dimension of ANSI C57.12.26 figures 2 and 4.
4.5.3.6 | The switching compartment door shall be capable of being closed and locked when elbows of the H.V.cable and grounding elbows are inserted into the feed-thru connectors.
4.5.3.7 | Provided with a pull-ring type automatic pressure relief system with means for manual operation in accordance to ANSl.
4.5.3.8 | Provided with two 25 mm (1 inch) minimum brass pipe plugs or fittings for filing,draining and pressure testing.
4.5.3.9 | Provided with a temperature gauge.
4.5.3.10 | Provided with a magnetic type insulating fluid level gauge; the gauge shall not show residual fuid liquid levels if the fluid level is below the gauge
4.5.3.11 | Provided with the protective caps to cover unused bushing well inserts.
4.5.3.12 | Provided with two (2) position load break switches
4.5.3.13 | Provided with one (1) oil-immersed arrestor with a positive disconnected fluid
4.5.4 Insulating Fluid
4.5.4.1 | The transformer shall be furnished with new, unused mineral oil. Less than 40kV, when tested inaccordance to ASTM D1816 using 2mm electrode spacing
4.5.4.2 | Provide insulating fluid certified to be PCB free when tested in accordance with Ontario Hydro Specification M-104M-85
4.5.4.3 | The type of insulating fluid used is to be stenciled on the inside of the transfomer switching compartment cover in the bold 25mm letters
4.5.5 Drip Tray
4.5.5.1 | A fixed tray, designed to retain 100ml of insulating fluid and prevent the fluid from dripping down the tank wall or onto accessories, shall be installed below the location of each withdrawable fuse. Owner approved removal oil-absorbent material shall be installed in the tray.Water running down the tank wall shall not collect in the trays.
4.5.5.2 | In all instances,the design of the withdrawable fuse assembly shall be such that repeated insertions and withdrawal of the fuse cannot result in loosening or detachment of any parts.
4.5.6 Tap Changer
4.5.6 | All tap leads shall be brought to a tap changer inside the transformer tank. Tap changer shall be externally operated and provided with a lockable handle and plate clearly designated by number or letters the tap setting. Such designation will be easily identified with voltage of the tap shown on the name-plate.The operating handle shall be installed in the cable entrance compartment at such a location that it is visible and accessible with cables in place and handleshall be capable of being locked in any position. Tap changer will be operated only with the transformer de-energized.Tap changer shall meet requirements of ANSI C57.12.10 paragraph 9.2.1.All transformers are required to have taps of 2.5 percent and 5 percent above and below nominal rated primary voltage that shall operate on all voltage positions for muli-voltage units. The tap position must be clearly identified in the cable compartment by a suitable method such that,the identification marks provided and furnished with a separate warning sign mounted close to the operating handle,cannot be removed under any operating conditions and last the life of the transformer under normal operating conditions.Letterings are to be 15-25 mm high.
4.5.7 Connections and Terminations
4.5.7.1 | Each unit shall be supplied with terminals for loop feed pad-mounted transformers.Six high-voltage bushing wells equipped with parking stands shall be supplied. Low-voltage bushings and high-voltage bushing wells shall be replaceable without removing the core and coil assembly from the tank.
4.5.7.2 High Voltage Terminations | Each transformershall be equipped with two (2)200A fully insulated high- voltage bushing wells complete with inserts.The bushing well shall be Elastimold catalogue #K1601PC-S1 (or-T1)or approved equivalent and the insert Elastimold catalogue #2701A4 or approved equal. The high-voltage neutral shall be securely connected internally to the grounded clamping structure or the tank.This connection shall be independent of all other electrical connections.
4.5.7.3 Low Voltage Terminations | Each transformer shall be equipped with three(3)low-voltage tinned copper terminals of the spade-type,in accordance with ANSI Standards. The secondary terminals shall be capable of withstanding a minimum vertical cantilever force of 750N continuously applied at the outermost hole of the terminal without any fluid leakage,damage or permanent distortion to the teminal. The low-voltage neutral shall be connected to an insulated neutral terminal designated xz having a current-carrying capacity equal to the other low- voltage terminals. Low-voltage neutral shall be a fully insulated terminal. For the fully insulated terminal,a ground padshall be provided on the outer surface of the tank.One or more removable ground straps suitably sized for the short circuit rating of the transformer as defined in ANSI C57.12.00 shall be provided and connected between the low-voltage neutral terminal and the ground pad (ANSI C57.12.21-1992,6.2).
4.5.7.4 Grounding | A copper ground bus shall be mounted horizontally in the cable compartment on the lower front of the tank wall.The ground bus shall be drilled with four 15-mm diameter holes to allow ground connections. Low voltage bushings,600 volts and below,shall be equipped with spade type terminals,NEMA drlled.Spade size and ampacity to be determined by transformer rating.Clamp type terminals,complete with non-ferrous bolts,nuts,washers,and lock washers for attaching these teminals to the spadeshall be funished.The clamp type terminals shall be of the "Cable Range"type with maximum range exceeding the ampacity of cable(s) required to continuously carry ful load to the transformer,and shall be suitable for either copper or aluminum conductors.
4.5.8 Nameplate,Labels and Markings
4.5.8.1 Nameplate | The transfomer shall be provided with a nameplate containing all infomation,connection diagrams,etc.,in accordance with ANSI C57.12.00 paragraph 5.12.2.Nameplate shall be bar coded. In addition to the information to be contained in the combination nameplate and connection diagram as outlined in ANSl,the nameplateshall contain the following information: -Jamaica Public Service Company Ltd. Purchase Order Number -Total weight of the insulating liquid in kilograms -Total volume of the insulating liquid in litres -PCB content -Protective devices information The transformer nameplate and connection diagram shall be mounted on the cable entrance compartment of the transformer and shall be engraved such that the lettering will last the life of the transformer
4.5.8.2 Warnings and Labels
Warning Label -Tap Changer | A warning sign shall be mounted close to the tap changer handle and shall have engraved on it in bold 10 mm minimum letters in red over white background: OPERATE TAP CHANGER SWITCH ONLY WHEN TRANSFORMER IS DE-ENERGISED. Centre lettering vertically and horizontally with 3mm between lines.
Warning label -Withdraw able fuse | A warning sign shall be mounted close to the withdrawable bayonet fuse holder handle and shall have engraved on it in bold 10mm minimum letters in red over white background: DO NOT OPERATE FUSE ASSEMBLY UNLESS TRANSFORMER IS DE-ENERGISED. OPERATE PRESSURE RELIEF DEVICE FIRST BEFORE PULLING OUT BAYONET FUSE HOLDER. Centre lettering vertically and horizontally with 3mm between lines.
Hazard Warning Labels | Hazard warning signs confoming to EEMAC Standard L16-1 shall be afixed to the inside and outside of the compartment doors
4.5.8.3 Exterior Markings | A self-adhesive tag shall be externally attached to the side of the transformer in the upper left corner. it shall contain the following information: -Serial number -kVA -Manufacturer's Name/Logo - kV - Stock code number
4.5.8.4 High Voltage and Low Voltage Terminal Markings | The high and low voltage terminals shall be stenciled H1A, H1B and Xi, Xz, Xa,respectively. The high and low voltage terminals on the dual voltage transformershall be stenciled H1A, H1B, H2A, H2B and X1, X2, X3 , respectively.
4.5.9 Earthling Pads and Terminals | Tank grounding or earthling pads shall be provided according to ANSI C57.12.10 paragraph 9.28.One terminal suitable for both aluminum and copper conductors to permit the earthling of the transformer shall be furnished for range of sizes from 50 mm²to 120 mm²(1/0 AWG to 250 KCMIL)conductor
4.5.10 Cores | Cores shall be clamped and braced to resist distortion caused by short- circuit stresses or transportation handling and to prevent the shifting of core laminations. Cores shall be constructed of high-grade,grain oriented,cold rolled silicon steel laminations,with high magnetic permeability.Core construction shall include provisions that mitigate core losses,excitation current and noise levels. All standard accessories required by ANSl shall be furnished,in size and location on the units as detaiied in ANSI C57.12.10 paragraph 9.2.
4.5.11 Accessories
Each transformer shall be equipped with the following accessories:
4.5.11.1 Internal Fault Detection Device | Each transformer shall be equipped with a non-resettable device which detects and provides external indication of internal transformer faults,and also incorporates pressure relief functionality.The specification for the internal fault detection device shall be submitted for review at the time of tendering
4.5.11.2 High Voltage Load Break Switch | The transformer shall contain two(2)high voltage,single phase,liquid-immersed,load break switches. Switch 1 and 2 shall function as a continuous and load breaking device from source A,or Source B,or Source A and B-one for the loop feed and one for the transformer primary winding tap. These two position load break switches shall be clearly identified in the cable compartment by a suitable method such that the identification marks regardless of operating conditions is irremovable.
The switches shall have the following minimum electrical characteristics:
Electrical Characteristics
| a) | Voltage class | 15 kV
| b) | BIL | 150 kV
| c) | Continuous and Loadbreak current: | 300A
| d) | Interrupting Current: | 300A
| e) | Momentary,10 cycle
|  | Current: | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| f) | Close and Latch Current | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| g) | Operating Temperature: | 17℃ to 120℃
The contact speed of the switches shall be independent of operator speed.
4.5.11.3 Protective Devices
The transformershall be protected by a two-fuse protection system consisting of a bayonet oil-immersed,expulsion fuse in series with an oil-immersed,partial-range,current-limiting fuse.Bayonet fuse links shall sense both high currents and high oil temperature in order to provide thermal protection to the transformer. Coordinate transformer protection with expulsion fuse clearing low-current faults and current-limiting fuse clearing high-current faults beyond the interrupting rating of the expulsion fuse.In order to eliminate or minimize oil spills,the bayonet fuse assembly shall include an oil retention valve inside the housing that closes when the fuse holder is removed, and an external drip shield. The overall arrangement of the load break and protective devices shall allow loop feed to the transformer and prevent closing of the switch unto internal faults. Warning shall be displayed adjacent to the bayonet fuse cautioning against removing or inserting fuses unless the transformer has been de-energized and the tank pressure has been released as per JPS Specification # 6951-S-14 Section 4.5.11.1. The locking clips of the fuse holders,when locked in any positionshall not be damaged when closing the transformer hood. The fuse rating and manufacturer's Catalogue number of the bayonet fuse and current limiting fuse shall be identified on the combination nameplate
TESTS
5.1 | Tests defined in ANSI C57-1200 paragraph 9 shall be made in accordance with ANSI C57.12.90 by and at the expense of the manufacturer.
Production Tests
The manufacturer shall carry out standard Production Tests and,before shipment;the manufacturershall furnish certified copies of the test results for approval.No transformershall be shipped until tests results are received.Test shall include but not limited to the following:
5.1.1 | Excitation current at 100%and 110%rated voltage;test to be made with either the primary or secondary in open circuit.
5.1.2 | Winding Insulation Resistance
Losses Calculations
For the purpose of comparing Bids,the transformer losses will be evaluated on the following basis:- Evaluated cost of transformer (EC) EC = P+5.403*L1+2.412*L2 Where: EC is the evaluated cost in US$ P is CIF price of transformer in US$ Li is No Load Loss in Watts Lz is Load Loss in Watts, (On the “Transformer Data Fom”the maximum losses shall be quoted at specified voltage configuration.)

## 021802009004
Specifications | JPS Requirement |  |  | Supplier Response |  |  | Supporting Documentation Provided (Yes or No) | Location in Supporting Document. | COMMENTS
Description | TRANSFORMER, PAD MOUNTED, 37.5 KVA, SINGLE PHASE, 24/13.8KV GRDY, OIL IMMERSED, DEAD FRONT, SECONDARY VOLTAGE 240/120 V, JPS SPECIFICATION No. : 6951-S-14. | [8 empty] | Yes
Quantity | 2 | [8 empty] | No
Stock Number | 21802009004
Manufacturer
Country Of Origin
INCO Terms
Lead Time
Warranty | The minimum warranty period shall be 18 months from date of payment or 12 months in service, whichever occurs first. The transformer shall be guaranteed for a minimum of 3 years in normal operating conditions, against any manufacturing defects or design anomalies.
Standards
3.1.2 | Applicable parts of the following standards shall be observed in the design, manufacture, performance and tests:-
| a) | ANSI C57.12.00 Standard General Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers
| b) | ANSI C57.12.22-1989 Requirements for Pad Mounted, Compartmental- Type, Self Cooled, Three Phase Distribution Transformers with High-Voltage Bushings, 2500 kVA and Smaller: High Voltage, 34 500 GrY/1920 Volts and Below; Low Voltage, 480 Volts and Below.
| c) | ANSI C57.12.21-1992 Standard for Transformers – Pad –Mounted, Compartmental- type, Self Cooled, Single Phase Distribution Transformers with High Voltage Bushings; High Voltage 34 500 GrY/19 920 Volta and Below: Low Voltage, 240/120 Volts; 167 kVA and Smaller.
| d) | ANSI C57.12.10 Safety Requirements for transformers 230 kV and below 833/958 through 8333/10417 kVA, single phase and 750/862 through 60,000/80,000/100,000 kVA, three phase Without Load Tap Changing and 3750/4687 through 60,000/80,000/100,000 kVA with load Tap Changing.
| e) | ANSI C57.12.28-1988 Switchgear and Transformers - Pad Mounted Equipment-Enclosure Integrity.
| f) | ANSI C57.12.70 Terminal Markings and Connections for Distribution and Power Transformers.
| g) | ANSI C57.12.80 Standard Terminology for Power and Distribution Transformers.
| h) | ANSI C57.12.90-1993 Test Code for Liquid- Immersed Distribution, Power and Regulating Transformers and Guide for Short Circuit Testing of Distribution and Power Transformers.
| i) | ANSI Z55.1 Seafoam Green finishes for Industrial Apparatus and Equipment.
| j) | ANSI C57.92-1981 Guide for Loading Mineral Oil Immersed Power Transformers up to and including 100 MVA with 55 oC or 65 oC Average Winding Rise.
| k) | ASTM D1816 Test method of dielectric oil
| l) | CSA C50 Insulating oil, electrical for transformers and switches.
| m) | EEMAC B6-1 Insulating mineral oil for new electrical apparatus.
| n) | NEMA TR-1 Transformers, Regulators and Reactors.
| o) | NEMA TR-P9
| p) | Western Underground Standards, WUG 2.13 Rev 4
| q) | ANSI/IEEE 386-1977
| r) | American Welding Standard, AWS D1.1/D1.1 M: 2008
| s) | Ontario Hydro Specification M-104M-85
| t) | EEMAC Standard L16-1
| u) | NETA Inter-National Electrical Testing Association
4.1 Insulation and Impedance Ratings
kVA | 37.5
Polarity | Subtractive
Bushings | Two (2) fuly insulated primary high voltage bushing (one (1) ot facilitate loop feed arrangement).
Fuse | The transformers shall be manufactured with a two-fuse primary protection system (bayonet fuse and current- limiting fuse), with overload indicating device
Taps | Two (2) 2 1⁄2% primary taps above and below normal voltage. Taps shall be provided for both the primary voltage levels of the dual voltage transformer. |  |  | Number of Taps and Percentage below and above nominal voltage |  | Tap Operatining on both Voltage? (YES/NO)
Primary Voltage (kV) | 24/13.8 KV GRDY
BIL(kV) | 125
Insulation Class (kV) | 15
Secondary Voltage (Volts) | 120/240
BIL (kV) | 30
Insulation Class (kV) | 1.2
Frequency(Hz) | 50
Continuous rated capacity at 65℃ temperature rise | See Material Schedule for Quantities and Sizes
Impedance (Nominal) as per ANSI | 2.5% +/- 7.5% for 25 kVA or less
4.00% +/7.5% for 37.5 kVA - 167kVA
4.2 Losses
SIZE (KVA) | No Load |  | Full Load | No Load |  | Full Load
25 Single Voltage | 72 |  | 157
25 Dual Voltage | 78 |  | 165
37.5 Single Voltage | 95 |  | 280
37.5 Dual Voltage | 118 |  | 338
50 Single Voltage | 130 |  | 350
50 Dual Voltage | 116 |  | 445
100 Single Voltage | 205 |  | 801
100 Dual Voltage | 205 |  | 836
167 Dual Voltage | 303 |  | 1103
LOSSES | Each individual transformer manufactured shall be test for No Load (core) losses at 100% rated voltage,and for Load (copper)losses at 85 degrees Celsius and fulload current.These tests shall be conducted at the nominal tap setting.The test results for each transformer by serial number shall be forwarded to the Purchaser (Buyer)for evaluation purposes. A loss evaluation will be completed to determine the lowest responsible bidder with respect to the overall best interest of JPSCo. JPSCo will evaluate losses based .
4.3 Performance
4.3.7.Temperature Rise | The temperature rise measured by resistance method shall not exceed 65 ℃ at a maximum ambient temperature of 30°C when operating continuous at rated capacity.
4.3.8. Dielectric Strength | The temperature rise measured by resistance methodshall not exceed 65℃ at a maximum ambient temperature of 30C when operating continuous at rated capacity.
4.3.9. Overload Capacity | The transformers shall be able to carry overloads in accordance with requirements of ANSI C57.92,with moderate sacrifice of life expectancy.
4.4. Audible Sound
4.4 Audible Sound | The audible sound level of transfomers when operating at rated voltage,and measured as per ANSI C57.12.90 shall not exceed the stipulated sound levels indicated below
| Transformer Size kVA |  | Audible sound level dB (Max)
| 25 |  | 48
| 37.5 |  | 48
| 50 |  | 48
| 100 |  | 51
| 150 |  | 55
| 167 |  | 55
4.5 Construction
The Transformer shall be mechanically designed to ANSI requirements,unless otherwise specified
4.5.1 Dimensions | The overall dimensions of the transfomer and compartment shall be kept to a minimum. |  |  | Length (mm) | Width (mm) | Height (mm)
4.5.2 Exterior finish | Modestly sculptured corners and round edges are encouraged. The transformer and compartments shall be painted standard Sea foam Green as per CIL/Glidden,Guertin Brothers SP2422 or owner approved equivalent paint. There shall be no plates or exterior stenciling positioned on the outside of the transformer tank or switching compartment except for a small plate or decal showing the name of manufacturer and high voltage warning labels.
4.5.3 Tank Compartment Assembly
4.5.3.1 | Provision for lifting shall be provided and shall be adequately strengthened, sized and arranged on the tank to provide a suitable lift for the completely assembled unit. The transformer base shall be arranged so that the tank bottom does not touch the pad.
4.5.3.2 | The welding shall conform to AWS Standard.Diagonal break marks on large surfaces sharp edges and protruding parts shall be avoided where possible.
4.5.3.3 | The strength of the transformershall be as such to withstand a minimum gauge pressure of 70 kPa without leakage or pemanent distortion of the tank exceeding 0.25%of the diagonal dimension of the surface so affected.
4.5.3.4 | Provision for lifting shall be provided and shall be adequately strengthened,sized and arranged on the tank to provide a suitable lift for the completely assembled unit.The transformer baseshall be arranged so that the tank bottom does not touch the pad.
4.5.3.5 | Furnished with side mounted parking stand,the parking stand shall be between the two(2)High Voltage bushings. The parking stand shall have sufficient space around it to accommodate Elastimold Cat.#163FTR or equivalent feed- thrust.Bushing spacing shall meet the minimum dimension of ANSI C57.12.26 figures 2 and 4.
4.5.3.6 | The switching compartment door shall be capable of being closed and locked when elbows of the H.V.cable and grounding elbows are inserted into the feed-thru connectors.
4.5.3.7 | Provided with a pull-ring type automatic pressure relief system with means for manual operation in accordance to ANSl.
4.5.3.8 | Provided with two 25 mm (1 inch) minimum brass pipe plugs or fittings for filing,draining and pressure testing.
4.5.3.9 | Provided with a temperature gauge.
4.5.3.10 | Provided with a magnetic type insulating fluid level gauge; the gauge shall not show residual fuid liquid levels if the fluid level is below the gauge
4.5.3.11 | Provided with the protective caps to cover unused bushing well inserts.
4.5.3.12 | Provided with two (2) position load break switches
4.5.3.13 | Provided with one (1) oil-immersed arrestor with a positive disconnected fluid
4.5.4 Insulating Fluid
4.5.4.1 | The transformer shall be furnished with new, unused mineral oil. Less than 40kV, when tested inaccordance to ASTM D1816 using 2mm electrode spacing
4.5.4.2 | Provide insulating fluid certified to be PCB free when tested in accordance with Ontario Hydro Specification M-104M-85
4.5.4.3 | The type of insulating fluid used is to be stenciled on the inside of the transfomer switching compartment cover in the bold 25mm letters
4.5.5 Drip Tray
4.5.5.1 | A fixed tray, designed to retain 100ml of insulating fluid and prevent the fluid from dripping down the tank wall or onto accessories, shall be installed below the location of each withdrawable fuse. Owner approved removal oil-absorbent material shall be installed in the tray.Water running down the tank wall shall not collect in the trays.
4.5.5.2 | In all instances,the design of the withdrawable fuse assembly shall be such that repeated insertions and withdrawal of the fuse cannot result in loosening or detachment of any parts.
4.5.6 Tap Changer
4.5.6 | All tap leads shall be brought to a tap changer inside the transformer tank. Tap changer shall be externally operated and provided with a lockable handle and plate clearly designated by number or letters the tap setting. Such designation will be easily identified with voltage of the tap shown on the name-plate.The operating handle shall be installed in the cable entrance compartment at such a location that it is visible and accessible with cables in place and handleshall be capable of being locked in any position. Tap changer will be operated only with the transformer de-energized.Tap changer shall meet requirements of ANSI C57.12.10 paragraph 9.2.1.All transformers are required to have taps of 2.5 percent and 5 percent above and below nominal rated primary voltage that shall operate on all voltage positions for muli-voltage units. The tap position must be clearly identified in the cable compartment by a suitable method such that,the identification marks provided and furnished with a separate warning sign mounted close to the operating handle,cannot be removed under any operating conditions and last the life of the transformer under normal operating conditions.Letterings are to be 15-25 mm high.
4.5.7 Connections and Terminations
4.5.7.1 | Each unit shall be supplied with terminals for loop feed pad-mounted transformers.Six high-voltage bushing wells equipped with parking stands shall be supplied. Low-voltage bushings and high-voltage bushing wells shall be replaceable without removing the core and coil assembly from the tank.
4.5.7.2 High Voltage Terminations | Each transformershall be equipped with two (2)200A fully insulated high- voltage bushing wells complete with inserts.The bushing well shall be Elastimold catalogue #K1601PC-S1 (or-T1)or approved equivalent and the insert Elastimold catalogue #2701A4 or approved equal. The high-voltage neutral shall be securely connected internally to the grounded clamping structure or the tank.This connection shall be independent of all other electrical connections.
4.5.7.3 Low Voltage Terminations | Each transformer shall be equipped with three(3)low-voltage tinned copper terminals of the spade-type,in accordance with ANSI Standards. The secondary terminals shall be capable of withstanding a minimum vertical cantilever force of 750N continuously applied at the outermost hole of the terminal without any fluid leakage,damage or permanent distortion to the teminal. The low-voltage neutral shall be connected to an insulated neutral terminal designated xz having a current-carrying capacity equal to the other low- voltage terminals. Low-voltage neutral shall be a fully insulated terminal. For the fully insulated terminal,a ground padshall be provided on the outer surface of the tank.One or more removable ground straps suitably sized for the short circuit rating of the transformer as defined in ANSI C57.12.00 shall be provided and connected between the low-voltage neutral terminal and the ground pad (ANSI C57.12.21-1992,6.2).
4.5.7.4 Grounding | A copper ground bus shall be mounted horizontally in the cable compartment on the lower front of the tank wall.The ground bus shall be drilled with four 15-mm diameter holes to allow ground connections. Low voltage bushings,600 volts and below,shall be equipped with spade type terminals,NEMA drlled.Spade size and ampacity to be determined by transformer rating.Clamp type terminals,complete with non-ferrous bolts,nuts,washers,and lock washers for attaching these teminals to the spadeshall be funished.The clamp type terminals shall be of the "Cable Range"type with maximum range exceeding the ampacity of cable(s) required to continuously carry ful load to the transformer,and shall be suitable for either copper or aluminum conductors.
4.5.8 Nameplate,Labels and Markings
4.5.8.1 Nameplate | The transfomer shall be provided with a nameplate containing all infomation,connection diagrams,etc.,in accordance with ANSI C57.12.00 paragraph 5.12.2.Nameplate shall be bar coded. In addition to the information to be contained in the combination nameplate and connection diagram as outlined in ANSl,the nameplateshall contain the following information: -Jamaica Public Service Company Ltd. Purchase Order Number -Total weight of the insulating liquid in kilograms -Total volume of the insulating liquid in litres -PCB content -Protective devices information The transformer nameplate and connection diagram shall be mounted on the cable entrance compartment of the transformer and shall be engraved such that the lettering will last the life of the transformer
4.5.8.2 Warnings and Labels
Warning Label -Tap Changer | A warning sign shall be mounted close to the tap changer handle and shall have engraved on it in bold 10 mm minimum letters in red over white background: OPERATE TAP CHANGER SWITCH ONLY WHEN TRANSFORMER IS DE-ENERGISED. Centre lettering vertically and horizontally with 3mm between lines.
Warning label -Withdraw able fuse | A warning sign shall be mounted close to the withdrawable bayonet fuse holder handle and shall have engraved on it in bold 10mm minimum letters in red over white background: DO NOT OPERATE FUSE ASSEMBLY UNLESS TRANSFORMER IS DE-ENERGISED. OPERATE PRESSURE RELIEF DEVICE FIRST BEFORE PULLING OUT BAYONET FUSE HOLDER. Centre lettering vertically and horizontally with 3mm between lines.
Hazard Warning Labels | Hazard warning signs confoming to EEMAC Standard L16-1 shall be afixed to the inside and outside of the compartment doors
4.5.8.3 Exterior Markings | A self-adhesive tag shall be externally attached to the side of the transformer in the upper left corner. it shall contain the following information: -Serial number -kVA -Manufacturer's Name/Logo - kV - Stock code number
4.5.8.4 High Voltage and Low Voltage Terminal Markings | The high and low voltage terminals shall be stenciled H1A, H1B and Xi, Xz, Xa,respectively. The high and low voltage terminals on the dual voltage transformershall be stenciled H1A, H1B, H2A, H2B and X1, X2, X3 , respectively.
4.5.9 Earthling Pads and Terminals | Tank grounding or earthling pads shall be provided according to ANSI C57.12.10 paragraph 9.28.One terminal suitable for both aluminum and copper conductors to permit the earthling of the transformer shall be furnished for range of sizes from 50 mm²to 120 mm²(1/0 AWG to 250 KCMIL)conductor
4.5.10 Cores | Cores shall be clamped and braced to resist distortion caused by short- circuit stresses or transportation handling and to prevent the shifting of core laminations. Cores shall be constructed of high-grade,grain oriented,cold rolled silicon steel laminations,with high magnetic permeability.Core construction shall include provisions that mitigate core losses,excitation current and noise levels. All standard accessories required by ANSl shall be furnished,in size and location on the units as detaiied in ANSI C57.12.10 paragraph 9.2.
4.5.11 Accessories
Each transformer shall be equipped with the following accessories:
4.5.11.1 Internal Fault Detection Device | Each transformer shall be equipped with a non-resettable device which detects and provides external indication of internal transformer faults,and also incorporates pressure relief functionality.The specification for the internal fault detection device shall be submitted for review at the time of tendering
4.5.11.2 High Voltage Load Break Switch | The transformer shall contain two(2)high voltage,single phase,liquid-immersed,load break switches. Switch 1 and 2 shall function as a continuous and load breaking device from source A,or Source B,or Source A and B-one for the loop feed and one for the transformer primary winding tap. These two position load break switches shall be clearly identified in the cable compartment by a suitable method such that the identification marks regardless of operating conditions is irremovable.
The switches shall have the following minimum electrical characteristics:
Electrical Characteristics
| a) | Voltage class | 15 kV
| b) | BIL | 150 kV
| c) | Continuous and Loadbreak current: | 300A
| d) | Interrupting Current: | 300A
| e) | Momentary,10 cycle
|  | Current: | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| f) | Close and Latch Current | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| g) | Operating Temperature: | 17℃ to 120℃
The contact speed of the switches shall be independent of operator speed.
4.5.11.3 Protective Devices
The transformershall be protected by a two-fuse protection system consisting of a bayonet oil-immersed,expulsion fuse in series with an oil-immersed,partial-range,current-limiting fuse.Bayonet fuse links shall sense both high currents and high oil temperature in order to provide thermal protection to the transformer. Coordinate transformer protection with expulsion fuse clearing low-current faults and current-limiting fuse clearing high-current faults beyond the interrupting rating of the expulsion fuse.In order to eliminate or minimize oil spills,the bayonet fuse assembly shall include an oil retention valve inside the housing that closes when the fuse holder is removed, and an external drip shield. The overall arrangement of the load break and protective devices shall allow loop feed to the transformer and prevent closing of the switch unto internal faults. Warning shall be displayed adjacent to the bayonet fuse cautioning against removing or inserting fuses unless the transformer has been de-energized and the tank pressure has been released as per JPS Specification # 6951-S-14 Section 4.5.11.1. The locking clips of the fuse holders,when locked in any positionshall not be damaged when closing the transformer hood. The fuse rating and manufacturer's Catalogue number of the bayonet fuse and current limiting fuse shall be identified on the combination nameplate
TESTS
5.1 | Tests defined in ANSI C57-1200 paragraph 9 shall be made in accordance with ANSI C57.12.90 by and at the expense of the manufacturer.
Production Tests
The manufacturer shall carry out standard Production Tests and,before shipment;the manufacturershall furnish certified copies of the test results for approval.No transformershall be shipped until tests results are received.Test shall include but not limited to the following:
5.1.1 | Excitation current at 100%and 110%rated voltage;test to be made with either the primary or secondary in open circuit.
5.1.2 | Winding Insulation Resistance
Losses Calculations
For the purpose of comparing Bids,the transformer losses will be evaluated on the following basis:- Evaluated cost of transformer (EC) EC = P+5.403*L1+2.412*L2 Where: EC is the evaluated cost in US$ P is CIF price of transformer in US$ Li is No Load Loss in Watts Lz is Load Loss in Watts, (On the “Transformer Data Fom”the maximum losses shall be quoted at specified voltage configuration.)

## 021802009006
Specifications | JPS Requirement |  |  | Supplier Response |  |  | Supporting Documentation Provided (Yes or No) | Location in Supporting Document. | COMMENTS
Description | TRANSFORMER, PAD MOUNTED, 50 KVA, SINGLE PHASE, DEAD FRONT, DUAL PRIMARY VOLTAGE, 24/13.8 KV GRDY X 12/6.9 KV GRDY, OIL IMMERSED, DEAD FRONT, SECONDARY VOLTAGE 240/120 V, JPS SPECIFICATION No. : 6951-S-14. | [8 empty] | Yes
Quantity | 15 | [8 empty] | No
Stock Number | 21802009006
Manufacturer
Country Of Origin
INCO Terms
Lead Time
Warranty | The minimum warranty period shall be 18 months from date of payment or 12 months in service, whichever occurs first. The transformer shall be guaranteed for a minimum of 3 years in normal operating conditions, against any manufacturing defects or design anomalies.
Standards
3.1.2 | Applicable parts of the following standards shall be observed in the design, manufacture, performance and tests:-
| a) | ANSI C57.12.00 Standard General Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers
| b) | ANSI C57.12.22-1989 Requirements for Pad Mounted, Compartmental- Type, Self Cooled, Three Phase Distribution Transformers with High-Voltage Bushings, 2500 kVA and Smaller: High Voltage, 34 500 GrY/1920 Volts and Below; Low Voltage, 480 Volts and Below.
| c) | ANSI C57.12.21-1992 Standard for Transformers – Pad –Mounted, Compartmental- type, Self Cooled, Single Phase Distribution Transformers with High Voltage Bushings; High Voltage 34 500 GrY/19 920 Volta and Below: Low Voltage, 240/120 Volts; 167 kVA and Smaller.
| d) | ANSI C57.12.10 Safety Requirements for transformers 230 kV and below 833/958 through 8333/10417 kVA, single phase and 750/862 through 60,000/80,000/100,000 kVA, three phase Without Load Tap Changing and 3750/4687 through 60,000/80,000/100,000 kVA with load Tap Changing.
| e) | ANSI C57.12.28-1988 Switchgear and Transformers - Pad Mounted Equipment-Enclosure Integrity.
| f) | ANSI C57.12.70 Terminal Markings and Connections for Distribution and Power Transformers.
| g) | ANSI C57.12.80 Standard Terminology for Power and Distribution Transformers.
| h) | ANSI C57.12.90-1993 Test Code for Liquid- Immersed Distribution, Power and Regulating Transformers and Guide for Short Circuit Testing of Distribution and Power Transformers.
| i) | ANSI Z55.1 Seafoam Green finishes for Industrial Apparatus and Equipment.
| j) | ANSI C57.92-1981 Guide for Loading Mineral Oil Immersed Power Transformers up to and including 100 MVA with 55 oC or 65 oC Average Winding Rise.
| k) | ASTM D1816 Test method of dielectric oil
| l) | CSA C50 Insulating oil, electrical for transformers and switches.
| m) | EEMAC B6-1 Insulating mineral oil for new electrical apparatus.
| n) | NEMA TR-1 Transformers, Regulators and Reactors.
| o) | NEMA TR-P9
| p) | Western Underground Standards, WUG 2.13 Rev 4
| q) | ANSI/IEEE 386-1977
| r) | American Welding Standard, AWS D1.1/D1.1 M: 2008
| s) | Ontario Hydro Specification M-104M-85
| t) | EEMAC Standard L16-1
| u) | NETA Inter-National Electrical Testing Association
4.1 Insulation and Impedance Ratings
kVA | 50
Polarity | Subtractive
Bushings | Two (2) fuly insulated primary high voltage bushing (one (1) ot facilitate loop feed arrangement).
Fuse | The transformers shall be manufactured with a two-fuse primary protection system (bayonet fuse and current- limiting fuse), with overload indicating device
Taps | Two (2) 2 1⁄2% primary taps above and below normal voltage. Taps shall be provided for both the primary voltage levels of the dual voltage transformer. |  |  | Number of Taps and Percentage below and above nominal voltage |  | Tap Operatining on both Voltage? (YES/NO)
Primary Voltage (kV) | 24/13.8 KV GRDY X 12/6.9 KV GRDY
BIL(kV) | 125
Insulation Class (kV) | 15
Secondary Voltage (Volts) | 120/240
BIL (kV) | 30
Insulation Class (kV) | 1.2
Frequency(Hz) | 50
Continuous rated capacity at 65℃ temperature rise | See Material Schedule for Quantities and Sizes
Impedance (Nominal) as per ANSI | 2.5% +/- 7.5% for 25 kVA or less
4.00% +/7.5% for 37.5 kVA - 167kVA
4.2 Losses
SIZE (KVA) | No Load |  | Full Load | No Load |  | Full Load
25 Single Voltage | 72 |  | 157
25 Dual Voltage | 78 |  | 165
37.5 Single Voltage | 95 |  | 280
37.5 Dual Voltage | 118 |  | 338
50 Single Voltage | 130 |  | 350
50 Dual Voltage | 116 |  | 445
100 Single Voltage | 205 |  | 801
100 Dual Voltage | 205 |  | 836
167 Dual Voltage | 303 |  | 1103
LOSSES | Each individual transformer manufactured shall be test for No Load (core) losses at 100% rated voltage,and for Load (copper)losses at 85 degrees Celsius and fulload current.These tests shall be conducted at the nominal tap setting.The test results for each transformer by serial number shall be forwarded to the Purchaser (Buyer)for evaluation purposes. A loss evaluation will be completed to determine the lowest responsible bidder with respect to the overall best interest of JPSCo. JPSCo will evaluate losses based .
4.3 Performance
4.3.7.Temperature Rise | The temperature rise measured by resistance method shall not exceed 65 ℃ at a maximum ambient temperature of 30°C when operating continuous at rated capacity.
4.3.8. Dielectric Strength | The temperature rise measured by resistance methodshall not exceed 65℃ at a maximum ambient temperature of 30C when operating continuous at rated capacity.
4.3.9. Overload Capacity | The transformers shall be able to carry overloads in accordance with requirements of ANSI C57.92,with moderate sacrifice of life expectancy.
4.4. Audible Sound
4.4 Audible Sound | The audible sound level of transfomers when operating at rated voltage,and measured as per ANSI C57.12.90 shall not exceed the stipulated sound levels indicated below
| Transformer Size kVA |  | Audible sound level dB (Max)
| 25 |  | 48
| 37.5 |  | 48
| 50 |  | 48
| 100 |  | 51
| 150 |  | 55
| 167 |  | 55
4.5 Construction
The Transformer shall be mechanically designed to ANSI requirements,unless otherwise specified
4.5.1 Dimensions | The overall dimensions of the transfomer and compartment shall be kept to a minimum. |  |  | Length (mm) | Width (mm) | Height (mm)
4.5.2 Exterior finish | Modestly sculptured corners and round edges are encouraged. The transformer and compartments shall be painted standard Sea foam Green as per CIL/Glidden,Guertin Brothers SP2422 or owner approved equivalent paint. There shall be no plates or exterior stenciling positioned on the outside of the transformer tank or switching compartment except for a small plate or decal showing the name of manufacturer and high voltage warning labels.
4.5.3 Tank Compartment Assembly
4.5.3.1 | Provision for lifting shall be provided and shall be adequately strengthened, sized and arranged on the tank to provide a suitable lift for the completely assembled unit. The transformer base shall be arranged so that the tank bottom does not touch the pad.
4.5.3.2 | The welding shall conform to AWS Standard.Diagonal break marks on large surfaces sharp edges and protruding parts shall be avoided where possible.
4.5.3.3 | The strength of the transformershall be as such to withstand a minimum gauge pressure of 70 kPa without leakage or pemanent distortion of the tank exceeding 0.25%of the diagonal dimension of the surface so affected.
4.5.3.4 | Provision for lifting shall be provided and shall be adequately strengthened,sized and arranged on the tank to provide a suitable lift for the completely assembled unit.The transformer baseshall be arranged so that the tank bottom does not touch the pad.
4.5.3.5 | Furnished with side mounted parking stand,the parking stand shall be between the two(2)High Voltage bushings. The parking stand shall have sufficient space around it to accommodate Elastimold Cat.#163FTR or equivalent feed- thrust.Bushing spacing shall meet the minimum dimension of ANSI C57.12.26 figures 2 and 4.
4.5.3.6 | The switching compartment door shall be capable of being closed and locked when elbows of the H.V.cable and grounding elbows are inserted into the feed-thru connectors.
4.5.3.7 | Provided with a pull-ring type automatic pressure relief system with means for manual operation in accordance to ANSl.
4.5.3.8 | Provided with two 25 mm (1 inch) minimum brass pipe plugs or fittings for filing,draining and pressure testing.
4.5.3.9 | Provided with a temperature gauge.
4.5.3.10 | Provided with a magnetic type insulating fluid level gauge; the gauge shall not show residual fuid liquid levels if the fluid level is below the gauge
4.5.3.11 | Provided with the protective caps to cover unused bushing well inserts.
4.5.3.12 | Provided with two (2) position load break switches
4.5.3.13 | Provided with one (1) oil-immersed arrestor with a positive disconnected fluid
4.5.4 Insulating Fluid
4.5.4.1 | The transformer shall be furnished with new, unused mineral oil. Less than 40kV, when tested inaccordance to ASTM D1816 using 2mm electrode spacing
4.5.4.2 | Provide insulating fluid certified to be PCB free when tested in accordance with Ontario Hydro Specification M-104M-85
4.5.4.3 | The type of insulating fluid used is to be stenciled on the inside of the transfomer switching compartment cover in the bold 25mm letters
4.5.5 Drip Tray
4.5.5.1 | A fixed tray, designed to retain 100ml of insulating fluid and prevent the fluid from dripping down the tank wall or onto accessories, shall be installed below the location of each withdrawable fuse. Owner approved removal oil-absorbent material shall be installed in the tray.Water running down the tank wall shall not collect in the trays.
4.5.5.2 | In all instances,the design of the withdrawable fuse assembly shall be such that repeated insertions and withdrawal of the fuse cannot result in loosening or detachment of any parts.
4.5.6 Tap Changer
4.5.6 | All tap leads shall be brought to a tap changer inside the transformer tank. Tap changer shall be externally operated and provided with a lockable handle and plate clearly designated by number or letters the tap setting. Such designation will be easily identified with voltage of the tap shown on the name-plate.The operating handle shall be installed in the cable entrance compartment at such a location that it is visible and accessible with cables in place and handleshall be capable of being locked in any position. Tap changer will be operated only with the transformer de-energized.Tap changer shall meet requirements of ANSI C57.12.10 paragraph 9.2.1.All transformers are required to have taps of 2.5 percent and 5 percent above and below nominal rated primary voltage that shall operate on all voltage positions for muli-voltage units. The tap position must be clearly identified in the cable compartment by a suitable method such that,the identification marks provided and furnished with a separate warning sign mounted close to the operating handle,cannot be removed under any operating conditions and last the life of the transformer under normal operating conditions.Letterings are to be 15-25 mm high.
4.5.7 Connections and Terminations
4.5.7.1 | Each unit shall be supplied with terminals for loop feed pad-mounted transformers.Six high-voltage bushing wells equipped with parking stands shall be supplied. Low-voltage bushings and high-voltage bushing wells shall be replaceable without removing the core and coil assembly from the tank.
4.5.7.2 High Voltage Terminations | Each transformershall be equipped with two (2)200A fully insulated high- voltage bushing wells complete with inserts.The bushing well shall be Elastimold catalogue #K1601PC-S1 (or-T1)or approved equivalent and the insert Elastimold catalogue #2701A4 or approved equal. The high-voltage neutral shall be securely connected internally to the grounded clamping structure or the tank.This connection shall be independent of all other electrical connections.
4.5.7.3 Low Voltage Terminations | Each transformer shall be equipped with three(3)low-voltage tinned copper terminals of the spade-type,in accordance with ANSI Standards. The secondary terminals shall be capable of withstanding a minimum vertical cantilever force of 750N continuously applied at the outermost hole of the terminal without any fluid leakage,damage or permanent distortion to the teminal. The low-voltage neutral shall be connected to an insulated neutral terminal designated xz having a current-carrying capacity equal to the other low- voltage terminals. Low-voltage neutral shall be a fully insulated terminal. For the fully insulated terminal,a ground padshall be provided on the outer surface of the tank.One or more removable ground straps suitably sized for the short circuit rating of the transformer as defined in ANSI C57.12.00 shall be provided and connected between the low-voltage neutral terminal and the ground pad (ANSI C57.12.21-1992,6.2).
4.5.7.4 Grounding | A copper ground bus shall be mounted horizontally in the cable compartment on the lower front of the tank wall.The ground bus shall be drilled with four 15-mm diameter holes to allow ground connections. Low voltage bushings,600 volts and below,shall be equipped with spade type terminals,NEMA drlled.Spade size and ampacity to be determined by transformer rating.Clamp type terminals,complete with non-ferrous bolts,nuts,washers,and lock washers for attaching these teminals to the spadeshall be funished.The clamp type terminals shall be of the "Cable Range"type with maximum range exceeding the ampacity of cable(s) required to continuously carry ful load to the transformer,and shall be suitable for either copper or aluminum conductors.
4.5.8 Nameplate,Labels and Markings
4.5.8.1 Nameplate | The transfomer shall be provided with a nameplate containing all infomation,connection diagrams,etc.,in accordance with ANSI C57.12.00 paragraph 5.12.2.Nameplate shall be bar coded. In addition to the information to be contained in the combination nameplate and connection diagram as outlined in ANSl,the nameplateshall contain the following information: -Jamaica Public Service Company Ltd. Purchase Order Number -Total weight of the insulating liquid in kilograms -Total volume of the insulating liquid in litres -PCB content -Protective devices information The transformer nameplate and connection diagram shall be mounted on the cable entrance compartment of the transformer and shall be engraved such that the lettering will last the life of the transformer
4.5.8.2 Warnings and Labels
Warning Label -Tap Changer | A warning sign shall be mounted close to the tap changer handle and shall have engraved on it in bold 10 mm minimum letters in red over white background: OPERATE TAP CHANGER SWITCH ONLY WHEN TRANSFORMER IS DE-ENERGISED. Centre lettering vertically and horizontally with 3mm between lines.
Warning label -Withdraw able fuse | A warning sign shall be mounted close to the withdrawable bayonet fuse holder handle and shall have engraved on it in bold 10mm minimum letters in red over white background: DO NOT OPERATE FUSE ASSEMBLY UNLESS TRANSFORMER IS DE-ENERGISED. OPERATE PRESSURE RELIEF DEVICE FIRST BEFORE PULLING OUT BAYONET FUSE HOLDER. Centre lettering vertically and horizontally with 3mm between lines.
Hazard Warning Labels | Hazard warning signs confoming to EEMAC Standard L16-1 shall be afixed to the inside and outside of the compartment doors
4.5.8.3 Exterior Markings | A self-adhesive tag shall be externally attached to the side of the transformer in the upper left corner. it shall contain the following information: -Serial number -kVA -Manufacturer's Name/Logo - kV - Stock code number
4.5.8.4 High Voltage and Low Voltage Terminal Markings | The high and low voltage terminals shall be stenciled H1A, H1B and Xi, Xz, Xa,respectively. The high and low voltage terminals on the dual voltage transformershall be stenciled H1A, H1B, H2A, H2B and X1, X2, X3 , respectively.
4.5.9 Earthling Pads and Terminals | Tank grounding or earthling pads shall be provided according to ANSI C57.12.10 paragraph 9.28.One terminal suitable for both aluminum and copper conductors to permit the earthling of the transformer shall be furnished for range of sizes from 50 mm²to 120 mm²(1/0 AWG to 250 KCMIL)conductor
4.5.10 Cores | Cores shall be clamped and braced to resist distortion caused by short- circuit stresses or transportation handling and to prevent the shifting of core laminations. Cores shall be constructed of high-grade,grain oriented,cold rolled silicon steel laminations,with high magnetic permeability.Core construction shall include provisions that mitigate core losses,excitation current and noise levels. All standard accessories required by ANSl shall be furnished,in size and location on the units as detaiied in ANSI C57.12.10 paragraph 9.2.
4.5.11 Accessories
Each transformer shall be equipped with the following accessories:
4.5.11.1 Internal Fault Detection Device | Each transformer shall be equipped with a non-resettable device which detects and provides external indication of internal transformer faults,and also incorporates pressure relief functionality.The specification for the internal fault detection device shall be submitted for review at the time of tendering
4.5.11.2 High Voltage Load Break Switch | The transformer shall contain two(2)high voltage,single phase,liquid-immersed,load break switches. Switch 1 and 2 shall function as a continuous and load breaking device from source A,or Source B,or Source A and B-one for the loop feed and one for the transformer primary winding tap. These two position load break switches shall be clearly identified in the cable compartment by a suitable method such that the identification marks regardless of operating conditions is irremovable.
The switches shall have the following minimum electrical characteristics:
Electrical Characteristics
| a) | Voltage class | 15 kV
| b) | BIL | 150 kV
| c) | Continuous and Loadbreak current: | 300A
| d) | Interrupting Current: | 300A
| e) | Momentary,10 cycle
|  | Current: | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| f) | Close and Latch Current | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| g) | Operating Temperature: | 17℃ to 120℃
The contact speed of the switches shall be independent of operator speed.
4.5.11.3 Protective Devices
The transformershall be protected by a two-fuse protection system consisting of a bayonet oil-immersed,expulsion fuse in series with an oil-immersed,partial-range,current-limiting fuse.Bayonet fuse links shall sense both high currents and high oil temperature in order to provide thermal protection to the transformer. Coordinate transformer protection with expulsion fuse clearing low-current faults and current-limiting fuse clearing high-current faults beyond the interrupting rating of the expulsion fuse.In order to eliminate or minimize oil spills,the bayonet fuse assembly shall include an oil retention valve inside the housing that closes when the fuse holder is removed, and an external drip shield. The overall arrangement of the load break and protective devices shall allow loop feed to the transformer and prevent closing of the switch unto internal faults. Warning shall be displayed adjacent to the bayonet fuse cautioning against removing or inserting fuses unless the transformer has been de-energized and the tank pressure has been released as per JPS Specification # 6951-S-14 Section 4.5.11.1. The locking clips of the fuse holders,when locked in any positionshall not be damaged when closing the transformer hood. The fuse rating and manufacturer's Catalogue number of the bayonet fuse and current limiting fuse shall be identified on the combination nameplate
TESTS
5.1 | Tests defined in ANSI C57-1200 paragraph 9 shall be made in accordance with ANSI C57.12.90 by and at the expense of the manufacturer.
Production Tests
The manufacturer shall carry out standard Production Tests and,before shipment;the manufacturershall furnish certified copies of the test results for approval.No transformershall be shipped until tests results are received.Test shall include but not limited to the following:
5.1.1 | Excitation current at 100%and 110%rated voltage;test to be made with either the primary or secondary in open circuit.
5.1.2 | Winding Insulation Resistance
Losses Calculations
For the purpose of comparing Bids,the transformer losses will be evaluated on the following basis:- Evaluated cost of transformer (EC) EC = P+5.403*L1+2.412*L2 Where: EC is the evaluated cost in US$ P is CIF price of transformer in US$ Li is No Load Loss in Watts Lz is Load Loss in Watts, (On the “Transformer Data Fom”the maximum losses shall be quoted at specified voltage configuration.)

## 021802009007
Specifications | JPS Requirement |  |  | Supplier Response |  |  | Supporting Documentation Provided (Yes or No) | Location in Supporting Document. | COMMENTS
Description | TRANSFORMER, PAD MOUNTED, 50 KVA, SINGLE PHASE, 24/13.8 KV GRDY, SINGLE PRIMARY VOLTAGE, OIL IMMERSED, DEAD FRONT, SECONDARY VOLTAGE 240/120 V, JPS SPECIFICATION No. : 6951-S-14. | [8 empty] | Yes
Quantity | 3 | [8 empty] | No
Stock Number | 21802009007
Manufacturer
Country Of Origin
INCO Terms
Lead Time
Warranty | The minimum warranty period shall be 18 months from date of payment or 12 months in service, whichever occurs first. The transformer shall be guaranteed for a minimum of 3 years in normal operating conditions, against any manufacturing defects or design anomalies.
Standards
3.1.2 | Applicable parts of the following standards shall be observed in the design, manufacture, performance and tests:-
| a) | ANSI C57.12.00 Standard General Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers
| b) | ANSI C57.12.22-1989 Requirements for Pad Mounted, Compartmental- Type, Self Cooled, Three Phase Distribution Transformers with High-Voltage Bushings, 2500 kVA and Smaller: High Voltage, 34 500 GrY/1920 Volts and Below; Low Voltage, 480 Volts and Below.
| c) | ANSI C57.12.21-1992 Standard for Transformers – Pad –Mounted, Compartmental- type, Self Cooled, Single Phase Distribution Transformers with High Voltage Bushings; High Voltage 34 500 GrY/19 920 Volta and Below: Low Voltage, 240/120 Volts; 167 kVA and Smaller.
| d) | ANSI C57.12.10 Safety Requirements for transformers 230 kV and below 833/958 through 8333/10417 kVA, single phase and 750/862 through 60,000/80,000/100,000 kVA, three phase Without Load Tap Changing and 3750/4687 through 60,000/80,000/100,000 kVA with load Tap Changing.
| e) | ANSI C57.12.28-1988 Switchgear and Transformers - Pad Mounted Equipment-Enclosure Integrity.
| f) | ANSI C57.12.70 Terminal Markings and Connections for Distribution and Power Transformers.
| g) | ANSI C57.12.80 Standard Terminology for Power and Distribution Transformers.
| h) | ANSI C57.12.90-1993 Test Code for Liquid- Immersed Distribution, Power and Regulating Transformers and Guide for Short Circuit Testing of Distribution and Power Transformers.
| i) | ANSI Z55.1 Seafoam Green finishes for Industrial Apparatus and Equipment.
| j) | ANSI C57.92-1981 Guide for Loading Mineral Oil Immersed Power Transformers up to and including 100 MVA with 55 oC or 65 oC Average Winding Rise.
| k) | ASTM D1816 Test method of dielectric oil
| l) | CSA C50 Insulating oil, electrical for transformers and switches.
| m) | EEMAC B6-1 Insulating mineral oil for new electrical apparatus.
| n) | NEMA TR-1 Transformers, Regulators and Reactors.
| o) | NEMA TR-P9
| p) | Western Underground Standards, WUG 2.13 Rev 4
| q) | ANSI/IEEE 386-1977
| r) | American Welding Standard, AWS D1.1/D1.1 M: 2008
| s) | Ontario Hydro Specification M-104M-85
| t) | EEMAC Standard L16-1
| u) | NETA Inter-National Electrical Testing Association
4.1 Insulation and Impedance Ratings
kVA | 50
Polarity | Subtractive
Bushings | Two (2) fuly insulated primary high voltage bushing (one (1) ot facilitate loop feed arrangement).
Fuse | The transformers shall be manufactured with a two-fuse primary protection system (bayonet fuse and current- limiting fuse), with overload indicating device
Taps | Two (2) 2 1⁄2% primary taps above and below normal voltage. Taps shall be provided for both the primary voltage levels of the dual voltage transformer. |  |  | Number of Taps and Percentage below and above nominal voltage |  | Tap Operatining on both Voltage? (YES/NO)
Primary Voltage (kV) | 24/13.8 KV GRDY
BIL(kV) | 125
Insulation Class (kV) | 15
Secondary Voltage (Volts) | 120/240
BIL (kV) | 30
Insulation Class (kV) | 1.2
Frequency(Hz) | 50
Continuous rated capacity at 65℃ temperature rise | See Material Schedule for Quantities and Sizes
Impedance (Nominal) as per ANSI | 2.5% +/- 7.5% for 25 kVA or less
4.00% +/7.5% for 37.5 kVA - 167kVA
4.2 Losses
SIZE (KVA) | No Load |  | Full Load | No Load |  | Full Load
25 Single Voltage | 72 |  | 157
25 Dual Voltage | 78 |  | 165
37.5 Single Voltage | 95 |  | 280
37.5 Dual Voltage | 118 |  | 338
50 Single Voltage | 130 |  | 350
50 Dual Voltage | 116 |  | 445
100 Single Voltage | 205 |  | 801
100 Dual Voltage | 205 |  | 836
167 Dual Voltage | 303 |  | 1103
LOSSES | Each individual transformer manufactured shall be test for No Load (core) losses at 100% rated voltage,and for Load (copper)losses at 85 degrees Celsius and fulload current.These tests shall be conducted at the nominal tap setting.The test results for each transformer by serial number shall be forwarded to the Purchaser (Buyer)for evaluation purposes. A loss evaluation will be completed to determine the lowest responsible bidder with respect to the overall best interest of JPSCo. JPSCo will evaluate losses based .
4.3 Performance
4.3.7.Temperature Rise | The temperature rise measured by resistance method shall not exceed 65 ℃ at a maximum ambient temperature of 30°C when operating continuous at rated capacity.
4.3.8. Dielectric Strength | The temperature rise measured by resistance methodshall not exceed 65℃ at a maximum ambient temperature of 30C when operating continuous at rated capacity.
4.3.9. Overload Capacity | The transformers shall be able to carry overloads in accordance with requirements of ANSI C57.92,with moderate sacrifice of life expectancy.
4.4. Audible Sound
4.4 Audible Sound | The audible sound level of transfomers when operating at rated voltage,and measured as per ANSI C57.12.90 shall not exceed the stipulated sound levels indicated below
| Transformer Size kVA |  | Audible sound level dB (Max)
| 25 |  | 48
| 37.5 |  | 48
| 50 |  | 48
| 100 |  | 51
| 150 |  | 55
| 167 |  | 55
4.5 Construction
The Transformer shall be mechanically designed to ANSI requirements,unless otherwise specified
4.5.1 Dimensions | The overall dimensions of the transfomer and compartment shall be kept to a minimum. |  |  | Length (mm) | Width (mm) | Height (mm)
4.5.2 Exterior finish | Modestly sculptured corners and round edges are encouraged. The transformer and compartments shall be painted standard Sea foam Green as per CIL/Glidden,Guertin Brothers SP2422 or owner approved equivalent paint. There shall be no plates or exterior stenciling positioned on the outside of the transformer tank or switching compartment except for a small plate or decal showing the name of manufacturer and high voltage warning labels.
4.5.3 Tank Compartment Assembly
4.5.3.1 | Provision for lifting shall be provided and shall be adequately strengthened, sized and arranged on the tank to provide a suitable lift for the completely assembled unit. The transformer base shall be arranged so that the tank bottom does not touch the pad.
4.5.3.2 | The welding shall conform to AWS Standard.Diagonal break marks on large surfaces sharp edges and protruding parts shall be avoided where possible.
4.5.3.3 | The strength of the transformershall be as such to withstand a minimum gauge pressure of 70 kPa without leakage or pemanent distortion of the tank exceeding 0.25%of the diagonal dimension of the surface so affected.
4.5.3.4 | Provision for lifting shall be provided and shall be adequately strengthened,sized and arranged on the tank to provide a suitable lift for the completely assembled unit.The transformer baseshall be arranged so that the tank bottom does not touch the pad.
4.5.3.5 | Furnished with side mounted parking stand,the parking stand shall be between the two(2)High Voltage bushings. The parking stand shall have sufficient space around it to accommodate Elastimold Cat.#163FTR or equivalent feed- thrust.Bushing spacing shall meet the minimum dimension of ANSI C57.12.26 figures 2 and 4.
4.5.3.6 | The switching compartment door shall be capable of being closed and locked when elbows of the H.V.cable and grounding elbows are inserted into the feed-thru connectors.
4.5.3.7 | Provided with a pull-ring type automatic pressure relief system with means for manual operation in accordance to ANSl.
4.5.3.8 | Provided with two 25 mm (1 inch) minimum brass pipe plugs or fittings for filing,draining and pressure testing.
4.5.3.9 | Provided with a temperature gauge.
4.5.3.10 | Provided with a magnetic type insulating fluid level gauge; the gauge shall not show residual fuid liquid levels if the fluid level is below the gauge
4.5.3.11 | Provided with the protective caps to cover unused bushing well inserts.
4.5.3.12 | Provided with two (2) position load break switches
4.5.3.13 | Provided with one (1) oil-immersed arrestor with a positive disconnected fluid
4.5.4 Insulating Fluid
4.5.4.1 | The transformer shall be furnished with new, unused mineral oil. Less than 40kV, when tested inaccordance to ASTM D1816 using 2mm electrode spacing
4.5.4.2 | Provide insulating fluid certified to be PCB free when tested in accordance with Ontario Hydro Specification M-104M-85
4.5.4.3 | The type of insulating fluid used is to be stenciled on the inside of the transfomer switching compartment cover in the bold 25mm letters
4.5.5 Drip Tray
4.5.5.1 | A fixed tray, designed to retain 100ml of insulating fluid and prevent the fluid from dripping down the tank wall or onto accessories, shall be installed below the location of each withdrawable fuse. Owner approved removal oil-absorbent material shall be installed in the tray.Water running down the tank wall shall not collect in the trays.
4.5.5.2 | In all instances,the design of the withdrawable fuse assembly shall be such that repeated insertions and withdrawal of the fuse cannot result in loosening or detachment of any parts.
4.5.6 Tap Changer
4.5.6 | All tap leads shall be brought to a tap changer inside the transformer tank. Tap changer shall be externally operated and provided with a lockable handle and plate clearly designated by number or letters the tap setting. Such designation will be easily identified with voltage of the tap shown on the name-plate.The operating handle shall be installed in the cable entrance compartment at such a location that it is visible and accessible with cables in place and handleshall be capable of being locked in any position. Tap changer will be operated only with the transformer de-energized.Tap changer shall meet requirements of ANSI C57.12.10 paragraph 9.2.1.All transformers are required to have taps of 2.5 percent and 5 percent above and below nominal rated primary voltage that shall operate on all voltage positions for muli-voltage units. The tap position must be clearly identified in the cable compartment by a suitable method such that,the identification marks provided and furnished with a separate warning sign mounted close to the operating handle,cannot be removed under any operating conditions and last the life of the transformer under normal operating conditions.Letterings are to be 15-25 mm high.
4.5.7 Connections and Terminations
4.5.7.1 | Each unit shall be supplied with terminals for loop feed pad-mounted transformers.Six high-voltage bushing wells equipped with parking stands shall be supplied. Low-voltage bushings and high-voltage bushing wells shall be replaceable without removing the core and coil assembly from the tank.
4.5.7.2 High Voltage Terminations | Each transformershall be equipped with two (2)200A fully insulated high- voltage bushing wells complete with inserts.The bushing well shall be Elastimold catalogue #K1601PC-S1 (or-T1)or approved equivalent and the insert Elastimold catalogue #2701A4 or approved equal. The high-voltage neutral shall be securely connected internally to the grounded clamping structure or the tank.This connection shall be independent of all other electrical connections.
4.5.7.3 Low Voltage Terminations | Each transformer shall be equipped with three(3)low-voltage tinned copper terminals of the spade-type,in accordance with ANSI Standards. The secondary terminals shall be capable of withstanding a minimum vertical cantilever force of 750N continuously applied at the outermost hole of the terminal without any fluid leakage,damage or permanent distortion to the teminal. The low-voltage neutral shall be connected to an insulated neutral terminal designated xz having a current-carrying capacity equal to the other low- voltage terminals. Low-voltage neutral shall be a fully insulated terminal. For the fully insulated terminal,a ground padshall be provided on the outer surface of the tank.One or more removable ground straps suitably sized for the short circuit rating of the transformer as defined in ANSI C57.12.00 shall be provided and connected between the low-voltage neutral terminal and the ground pad (ANSI C57.12.21-1992,6.2).
4.5.7.4 Grounding | A copper ground bus shall be mounted horizontally in the cable compartment on the lower front of the tank wall.The ground bus shall be drilled with four 15-mm diameter holes to allow ground connections. Low voltage bushings,600 volts and below,shall be equipped with spade type terminals,NEMA drlled.Spade size and ampacity to be determined by transformer rating.Clamp type terminals,complete with non-ferrous bolts,nuts,washers,and lock washers for attaching these teminals to the spadeshall be funished.The clamp type terminals shall be of the "Cable Range"type with maximum range exceeding the ampacity of cable(s) required to continuously carry ful load to the transformer,and shall be suitable for either copper or aluminum conductors.
4.5.8 Nameplate,Labels and Markings
4.5.8.1 Nameplate | The transfomer shall be provided with a nameplate containing all infomation,connection diagrams,etc.,in accordance with ANSI C57.12.00 paragraph 5.12.2.Nameplate shall be bar coded. In addition to the information to be contained in the combination nameplate and connection diagram as outlined in ANSl,the nameplateshall contain the following information: -Jamaica Public Service Company Ltd. Purchase Order Number -Total weight of the insulating liquid in kilograms -Total volume of the insulating liquid in litres -PCB content -Protective devices information The transformer nameplate and connection diagram shall be mounted on the cable entrance compartment of the transformer and shall be engraved such that the lettering will last the life of the transformer
4.5.8.2 Warnings and Labels
Warning Label -Tap Changer | A warning sign shall be mounted close to the tap changer handle and shall have engraved on it in bold 10 mm minimum letters in red over white background: OPERATE TAP CHANGER SWITCH ONLY WHEN TRANSFORMER IS DE-ENERGISED. Centre lettering vertically and horizontally with 3mm between lines.
Warning label -Withdraw able fuse | A warning sign shall be mounted close to the withdrawable bayonet fuse holder handle and shall have engraved on it in bold 10mm minimum letters in red over white background: DO NOT OPERATE FUSE ASSEMBLY UNLESS TRANSFORMER IS DE-ENERGISED. OPERATE PRESSURE RELIEF DEVICE FIRST BEFORE PULLING OUT BAYONET FUSE HOLDER. Centre lettering vertically and horizontally with 3mm between lines.
Hazard Warning Labels | Hazard warning signs confoming to EEMAC Standard L16-1 shall be afixed to the inside and outside of the compartment doors
4.5.8.3 Exterior Markings | A self-adhesive tag shall be externally attached to the side of the transformer in the upper left corner. it shall contain the following information: -Serial number -kVA -Manufacturer's Name/Logo - kV - Stock code number
4.5.8.4 High Voltage and Low Voltage Terminal Markings | The high and low voltage terminals shall be stenciled H1A, H1B and Xi, Xz, Xa,respectively. The high and low voltage terminals on the dual voltage transformershall be stenciled H1A, H1B, H2A, H2B and X1, X2, X3 , respectively.
4.5.9 Earthling Pads and Terminals | Tank grounding or earthling pads shall be provided according to ANSI C57.12.10 paragraph 9.28.One terminal suitable for both aluminum and copper conductors to permit the earthling of the transformer shall be furnished for range of sizes from 50 mm²to 120 mm²(1/0 AWG to 250 KCMIL)conductor
4.5.10 Cores | Cores shall be clamped and braced to resist distortion caused by short- circuit stresses or transportation handling and to prevent the shifting of core laminations. Cores shall be constructed of high-grade,grain oriented,cold rolled silicon steel laminations,with high magnetic permeability.Core construction shall include provisions that mitigate core losses,excitation current and noise levels. All standard accessories required by ANSl shall be furnished,in size and location on the units as detaiied in ANSI C57.12.10 paragraph 9.2.
4.5.11 Accessories
Each transformer shall be equipped with the following accessories:
4.5.11.1 Internal Fault Detection Device | Each transformer shall be equipped with a non-resettable device which detects and provides external indication of internal transformer faults,and also incorporates pressure relief functionality.The specification for the internal fault detection device shall be submitted for review at the time of tendering
4.5.11.2 High Voltage Load Break Switch | The transformer shall contain two(2)high voltage,single phase,liquid-immersed,load break switches. Switch 1 and 2 shall function as a continuous and load breaking device from source A,or Source B,or Source A and B-one for the loop feed and one for the transformer primary winding tap. These two position load break switches shall be clearly identified in the cable compartment by a suitable method such that the identification marks regardless of operating conditions is irremovable.
The switches shall have the following minimum electrical characteristics:
Electrical Characteristics
| a) | Voltage class | 15 kV
| b) | BIL | 150 kV
| c) | Continuous and Loadbreak current: | 300A
| d) | Interrupting Current: | 300A
| e) | Momentary,10 cycle
|  | Current: | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| f) | Close and Latch Current | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| g) | Operating Temperature: | 17℃ to 120℃
The contact speed of the switches shall be independent of operator speed.
4.5.11.3 Protective Devices
The transformershall be protected by a two-fuse protection system consisting of a bayonet oil-immersed,expulsion fuse in series with an oil-immersed,partial-range,current-limiting fuse.Bayonet fuse links shall sense both high currents and high oil temperature in order to provide thermal protection to the transformer. Coordinate transformer protection with expulsion fuse clearing low-current faults and current-limiting fuse clearing high-current faults beyond the interrupting rating of the expulsion fuse.In order to eliminate or minimize oil spills,the bayonet fuse assembly shall include an oil retention valve inside the housing that closes when the fuse holder is removed, and an external drip shield. The overall arrangement of the load break and protective devices shall allow loop feed to the transformer and prevent closing of the switch unto internal faults. Warning shall be displayed adjacent to the bayonet fuse cautioning against removing or inserting fuses unless the transformer has been de-energized and the tank pressure has been released as per JPS Specification # 6951-S-14 Section 4.5.11.1. The locking clips of the fuse holders,when locked in any positionshall not be damaged when closing the transformer hood. The fuse rating and manufacturer's Catalogue number of the bayonet fuse and current limiting fuse shall be identified on the combination nameplate
TESTS
5.1 | Tests defined in ANSI C57-1200 paragraph 9 shall be made in accordance with ANSI C57.12.90 by and at the expense of the manufacturer.
Production Tests
The manufacturer shall carry out standard Production Tests and,before shipment;the manufacturershall furnish certified copies of the test results for approval.No transformershall be shipped until tests results are received.Test shall include but not limited to the following:
5.1.1 | Excitation current at 100%and 110%rated voltage;test to be made with either the primary or secondary in open circuit.
5.1.2 | Winding Insulation Resistance
Losses Calculations
For the purpose of comparing Bids,the transformer losses will be evaluated on the following basis:- Evaluated cost of transformer (EC) EC = P+5.403*L1+2.412*L2 Where: EC is the evaluated cost in US$ P is CIF price of transformer in US$ Li is No Load Loss in Watts Lz is Load Loss in Watts, (On the “Transformer Data Fom”the maximum losses shall be quoted at specified voltage configuration.)

## 021802009008
Specifications | JPS Requirement |  |  | Supplier Response |  |  | Supporting Documentation Provided (Yes or No) | Location in Supporting Document. | COMMENTS
Description | TRANSFORMER, PAD MOUNTED, 167 KVA, SINGLE PHASE, DUAL PRIMARY VOLTAGE, 24/13.8 KV GRDY X 12/6.9 KV GRDY, OIL IMMERSED DEAD FRONT, SECONDARY VOLTAGE 240/120 V, JPS SPECIFICATION No. : 6951-S-14. | [8 empty] | Yes
Quantity | 10 | [8 empty] | No
Stock Number | 21802009008
Manufacturer
Country Of Origin
INCO Terms
Lead Time
Warranty | The minimum warranty period shall be 18 months from date of payment or 12 months in service, whichever occurs first. The transformer shall be guaranteed for a minimum of 3 years in normal operating conditions, against any manufacturing defects or design anomalies.
Standards
3.1.2 | Applicable parts of the following standards shall be observed in the design, manufacture, performance and tests:-
| a) | ANSI C57.12.00 Standard General Requirements for Liquid-Immersed Distribution, Power and Regulating Transformers
| b) | ANSI C57.12.22-1989 Requirements for Pad Mounted, Compartmental- Type, Self Cooled, Three Phase Distribution Transformers with High-Voltage Bushings, 2500 kVA and Smaller: High Voltage, 34 500 GrY/1920 Volts and Below; Low Voltage, 480 Volts and Below.
| c) | ANSI C57.12.21-1992 Standard for Transformers – Pad –Mounted, Compartmental- type, Self Cooled, Single Phase Distribution Transformers with High Voltage Bushings; High Voltage 34 500 GrY/19 920 Volta and Below: Low Voltage, 240/120 Volts; 167 kVA and Smaller.
| d) | ANSI C57.12.10 Safety Requirements for transformers 230 kV and below 833/958 through 8333/10417 kVA, single phase and 750/862 through 60,000/80,000/100,000 kVA, three phase Without Load Tap Changing and 3750/4687 through 60,000/80,000/100,000 kVA with load Tap Changing.
| e) | ANSI C57.12.28-1988 Switchgear and Transformers - Pad Mounted Equipment-Enclosure Integrity.
| f) | ANSI C57.12.70 Terminal Markings and Connections for Distribution and Power Transformers.
| g) | ANSI C57.12.80 Standard Terminology for Power and Distribution Transformers.
| h) | ANSI C57.12.90-1993 Test Code for Liquid- Immersed Distribution, Power and Regulating Transformers and Guide for Short Circuit Testing of Distribution and Power Transformers.
| i) | ANSI Z55.1 Seafoam Green finishes for Industrial Apparatus and Equipment.
| j) | ANSI C57.92-1981 Guide for Loading Mineral Oil Immersed Power Transformers up to and including 100 MVA with 55 oC or 65 oC Average Winding Rise.
| k) | ASTM D1816 Test method of dielectric oil
| l) | CSA C50 Insulating oil, electrical for transformers and switches.
| m) | EEMAC B6-1 Insulating mineral oil for new electrical apparatus.
| n) | NEMA TR-1 Transformers, Regulators and Reactors.
| o) | NEMA TR-P9
| p) | Western Underground Standards, WUG 2.13 Rev 4
| q) | ANSI/IEEE 386-1977
| r) | American Welding Standard, AWS D1.1/D1.1 M: 2008
| s) | Ontario Hydro Specification M-104M-85
| t) | EEMAC Standard L16-1
| u) | NETA Inter-National Electrical Testing Association
4.1 Insulation and Impedance Ratings
kVA | 167
Polarity | Subtractive
Bushings | Two (2) fuly insulated primary high voltage bushing (one (1) ot facilitate loop feed arrangement).
Fuse | The transformers shall be manufactured with a two-fuse primary protection system (bayonet fuse and current- limiting fuse), with overload indicating device
Taps | Two (2) 2 1⁄2% primary taps above and below normal voltage. Taps shall be provided for both the primary voltage levels of the dual voltage transformer. |  |  | Number of Taps and Percentage below and above nominal voltage |  | Tap Operatining on both Voltage? (YES/NO)
Primary Voltage (kV) | 24/13.8 KV GRDY X 12/6.9 KV GRDY
BIL(kV) | 125
Insulation Class (kV) | 15
Secondary Voltage (Volts) | 120/240
BIL (kV) | 30
Insulation Class (kV) | 1.2
Frequency(Hz) | 50
Continuous rated capacity at 65℃ temperature rise | See Material Schedule for Quantities and Sizes
Impedance (Nominal) as per ANSI | 2.5% +/- 7.5% for 25 kVA or less
4.00% +/7.5% for 37.5 kVA - 167kVA
4.2 Losses
SIZE (KVA) | No Load |  | Full Load | No Load |  | Full Load
25 Single Voltage | 72 |  | 157
25 Dual Voltage | 78 |  | 165
37.5 Single Voltage | 95 |  | 280
37.5 Dual Voltage | 118 |  | 338
50 Single Voltage | 130 |  | 350
50 Dual Voltage | 116 |  | 445
100 Single Voltage | 205 |  | 801
100 Dual Voltage | 205 |  | 836
167 Dual Voltage | 303 |  | 1103
LOSSES | Each individual transformer manufactured shall be test for No Load (core) losses at 100% rated voltage,and for Load (copper)losses at 85 degrees Celsius and fulload current.These tests shall be conducted at the nominal tap setting.The test results for each transformer by serial number shall be forwarded to the Purchaser (Buyer)for evaluation purposes. A loss evaluation will be completed to determine the lowest responsible bidder with respect to the overall best interest of JPSCo. JPSCo will evaluate losses based .
4.3 Performance
4.3.7.Temperature Rise | The temperature rise measured by resistance method shall not exceed 65 ℃ at a maximum ambient temperature of 30°C when operating continuous at rated capacity.
4.3.8. Dielectric Strength | The temperature rise measured by resistance methodshall not exceed 65℃ at a maximum ambient temperature of 30C when operating continuous at rated capacity.
4.3.9. Overload Capacity | The transformers shall be able to carry overloads in accordance with requirements of ANSI C57.92,with moderate sacrifice of life expectancy.
4.4. Audible Sound
4.4 Audible Sound | The audible sound level of transfomers when operating at rated voltage,and measured as per ANSI C57.12.90 shall not exceed the stipulated sound levels indicated below
| Transformer Size kVA |  | Audible sound level dB (Max)
| 25 |  | 48
| 37.5 |  | 48
| 50 |  | 48
| 100 |  | 51
| 150 |  | 55
| 167 |  | 55
4.5 Construction
The Transformer shall be mechanically designed to ANSI requirements,unless otherwise specified
4.5.1 Dimensions | The overall dimensions of the transfomer and compartment shall be kept to a minimum. |  |  | Length (mm) | Width (mm) | Height (mm)
4.5.2 Exterior finish | Modestly sculptured corners and round edges are encouraged. The transformer and compartments shall be painted standard Sea foam Green as per CIL/Glidden,Guertin Brothers SP2422 or owner approved equivalent paint. There shall be no plates or exterior stenciling positioned on the outside of the transformer tank or switching compartment except for a small plate or decal showing the name of manufacturer and high voltage warning labels.
4.5.3 Tank Compartment Assembly
4.5.3.1 | Provision for lifting shall be provided and shall be adequately strengthened, sized and arranged on the tank to provide a suitable lift for the completely assembled unit. The transformer base shall be arranged so that the tank bottom does not touch the pad.
4.5.3.2 | The welding shall conform to AWS Standard.Diagonal break marks on large surfaces sharp edges and protruding parts shall be avoided where possible.
4.5.3.3 | The strength of the transformershall be as such to withstand a minimum gauge pressure of 70 kPa without leakage or pemanent distortion of the tank exceeding 0.25%of the diagonal dimension of the surface so affected.
4.5.3.4 | Provision for lifting shall be provided and shall be adequately strengthened,sized and arranged on the tank to provide a suitable lift for the completely assembled unit.The transformer baseshall be arranged so that the tank bottom does not touch the pad.
4.5.3.5 | Furnished with side mounted parking stand,the parking stand shall be between the two(2)High Voltage bushings. The parking stand shall have sufficient space around it to accommodate Elastimold Cat.#163FTR or equivalent feed- thrust.Bushing spacing shall meet the minimum dimension of ANSI C57.12.26 figures 2 and 4.
4.5.3.6 | The switching compartment door shall be capable of being closed and locked when elbows of the H.V.cable and grounding elbows are inserted into the feed-thru connectors.
4.5.3.7 | Provided with a pull-ring type automatic pressure relief system with means for manual operation in accordance to ANSl.
4.5.3.8 | Provided with two 25 mm (1 inch) minimum brass pipe plugs or fittings for filing,draining and pressure testing.
4.5.3.9 | Provided with a temperature gauge.
4.5.3.10 | Provided with a magnetic type insulating fluid level gauge; the gauge shall not show residual fuid liquid levels if the fluid level is below the gauge
4.5.3.11 | Provided with the protective caps to cover unused bushing well inserts.
4.5.3.12 | Provided with two (2) position load break switches
4.5.3.13 | Provided with one (1) oil-immersed arrestor with a positive disconnected fluid
4.5.4 Insulating Fluid
4.5.4.1 | The transformer shall be furnished with new, unused mineral oil. Less than 40kV, when tested inaccordance to ASTM D1816 using 2mm electrode spacing
4.5.4.2 | Provide insulating fluid certified to be PCB free when tested in accordance with Ontario Hydro Specification M-104M-85
4.5.4.3 | The type of insulating fluid used is to be stenciled on the inside of the transfomer switching compartment cover in the bold 25mm letters
4.5.5 Drip Tray
4.5.5.1 | A fixed tray, designed to retain 100ml of insulating fluid and prevent the fluid from dripping down the tank wall or onto accessories, shall be installed below the location of each withdrawable fuse. Owner approved removal oil-absorbent material shall be installed in the tray.Water running down the tank wall shall not collect in the trays.
4.5.5.2 | In all instances,the design of the withdrawable fuse assembly shall be such that repeated insertions and withdrawal of the fuse cannot result in loosening or detachment of any parts.
4.5.6 Tap Changer
4.5.6 | All tap leads shall be brought to a tap changer inside the transformer tank. Tap changer shall be externally operated and provided with a lockable handle and plate clearly designated by number or letters the tap setting. Such designation will be easily identified with voltage of the tap shown on the name-plate.The operating handle shall be installed in the cable entrance compartment at such a location that it is visible and accessible with cables in place and handleshall be capable of being locked in any position. Tap changer will be operated only with the transformer de-energized.Tap changer shall meet requirements of ANSI C57.12.10 paragraph 9.2.1.All transformers are required to have taps of 2.5 percent and 5 percent above and below nominal rated primary voltage that shall operate on all voltage positions for muli-voltage units. The tap position must be clearly identified in the cable compartment by a suitable method such that,the identification marks provided and furnished with a separate warning sign mounted close to the operating handle,cannot be removed under any operating conditions and last the life of the transformer under normal operating conditions.Letterings are to be 15-25 mm high.
4.5.7 Connections and Terminations
4.5.7.1 | Each unit shall be supplied with terminals for loop feed pad-mounted transformers.Six high-voltage bushing wells equipped with parking stands shall be supplied. Low-voltage bushings and high-voltage bushing wells shall be replaceable without removing the core and coil assembly from the tank.
4.5.7.2 High Voltage Terminations | Each transformershall be equipped with two (2)200A fully insulated high- voltage bushing wells complete with inserts.The bushing well shall be Elastimold catalogue #K1601PC-S1 (or-T1)or approved equivalent and the insert Elastimold catalogue #2701A4 or approved equal. The high-voltage neutral shall be securely connected internally to the grounded clamping structure or the tank.This connection shall be independent of all other electrical connections.
4.5.7.3 Low Voltage Terminations | Each transformer shall be equipped with three(3)low-voltage tinned copper terminals of the spade-type,in accordance with ANSI Standards. The secondary terminals shall be capable of withstanding a minimum vertical cantilever force of 750N continuously applied at the outermost hole of the terminal without any fluid leakage,damage or permanent distortion to the teminal. The low-voltage neutral shall be connected to an insulated neutral terminal designated xz having a current-carrying capacity equal to the other low- voltage terminals. Low-voltage neutral shall be a fully insulated terminal. For the fully insulated terminal,a ground padshall be provided on the outer surface of the tank.One or more removable ground straps suitably sized for the short circuit rating of the transformer as defined in ANSI C57.12.00 shall be provided and connected between the low-voltage neutral terminal and the ground pad (ANSI C57.12.21-1992,6.2).
4.5.7.4 Grounding | A copper ground bus shall be mounted horizontally in the cable compartment on the lower front of the tank wall.The ground bus shall be drilled with four 15-mm diameter holes to allow ground connections. Low voltage bushings,600 volts and below,shall be equipped with spade type terminals,NEMA drlled.Spade size and ampacity to be determined by transformer rating.Clamp type terminals,complete with non-ferrous bolts,nuts,washers,and lock washers for attaching these teminals to the spadeshall be funished.The clamp type terminals shall be of the "Cable Range"type with maximum range exceeding the ampacity of cable(s) required to continuously carry ful load to the transformer,and shall be suitable for either copper or aluminum conductors.
4.5.8 Nameplate,Labels and Markings
4.5.8.1 Nameplate | The transfomer shall be provided with a nameplate containing all infomation,connection diagrams,etc.,in accordance with ANSI C57.12.00 paragraph 5.12.2.Nameplate shall be bar coded. In addition to the information to be contained in the combination nameplate and connection diagram as outlined in ANSl,the nameplateshall contain the following information: -Jamaica Public Service Company Ltd. Purchase Order Number -Total weight of the insulating liquid in kilograms -Total volume of the insulating liquid in litres -PCB content -Protective devices information The transformer nameplate and connection diagram shall be mounted on the cable entrance compartment of the transformer and shall be engraved such that the lettering will last the life of the transformer
4.5.8.2 Warnings and Labels
Warning Label -Tap Changer | A warning sign shall be mounted close to the tap changer handle and shall have engraved on it in bold 10 mm minimum letters in red over white background: OPERATE TAP CHANGER SWITCH ONLY WHEN TRANSFORMER IS DE-ENERGISED. Centre lettering vertically and horizontally with 3mm between lines.
Warning label -Withdraw able fuse | A warning sign shall be mounted close to the withdrawable bayonet fuse holder handle and shall have engraved on it in bold 10mm minimum letters in red over white background: DO NOT OPERATE FUSE ASSEMBLY UNLESS TRANSFORMER IS DE-ENERGISED. OPERATE PRESSURE RELIEF DEVICE FIRST BEFORE PULLING OUT BAYONET FUSE HOLDER. Centre lettering vertically and horizontally with 3mm between lines.
Hazard Warning Labels | Hazard warning signs confoming to EEMAC Standard L16-1 shall be afixed to the inside and outside of the compartment doors
4.5.8.3 Exterior Markings | A self-adhesive tag shall be externally attached to the side of the transformer in the upper left corner. it shall contain the following information: -Serial number -kVA -Manufacturer's Name/Logo - kV - Stock code number
4.5.8.4 High Voltage and Low Voltage Terminal Markings | The high and low voltage terminals shall be stenciled H1A, H1B and Xi, Xz, Xa,respectively. The high and low voltage terminals on the dual voltage transformershall be stenciled H1A, H1B, H2A, H2B and X1, X2, X3 , respectively.
4.5.9 Earthling Pads and Terminals | Tank grounding or earthling pads shall be provided according to ANSI C57.12.10 paragraph 9.28.One terminal suitable for both aluminum and copper conductors to permit the earthling of the transformer shall be furnished for range of sizes from 50 mm²to 120 mm²(1/0 AWG to 250 KCMIL)conductor
4.5.10 Cores | Cores shall be clamped and braced to resist distortion caused by short- circuit stresses or transportation handling and to prevent the shifting of core laminations. Cores shall be constructed of high-grade,grain oriented,cold rolled silicon steel laminations,with high magnetic permeability.Core construction shall include provisions that mitigate core losses,excitation current and noise levels. All standard accessories required by ANSl shall be furnished,in size and location on the units as detaiied in ANSI C57.12.10 paragraph 9.2.
4.5.11 Accessories
Each transformer shall be equipped with the following accessories:
4.5.11.1 Internal Fault Detection Device | Each transformer shall be equipped with a non-resettable device which detects and provides external indication of internal transformer faults,and also incorporates pressure relief functionality.The specification for the internal fault detection device shall be submitted for review at the time of tendering
4.5.11.2 High Voltage Load Break Switch | The transformer shall contain two(2)high voltage,single phase,liquid-immersed,load break switches. Switch 1 and 2 shall function as a continuous and load breaking device from source A,or Source B,or Source A and B-one for the loop feed and one for the transformer primary winding tap. These two position load break switches shall be clearly identified in the cable compartment by a suitable method such that the identification marks regardless of operating conditions is irremovable.
The switches shall have the following minimum electrical characteristics:
Electrical Characteristics
| a) | Voltage class | 15 kV
| b) | BIL | 150 kV
| c) | Continuous and Loadbreak current: | 300A
| d) | Interrupting Current: | 300A
| e) | Momentary,10 cycle
|  | Current: | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| f) | Close and Latch Current | 12,000A ms.sys
|  | (X/R ratio =30) | 19,200A ms.asym
| g) | Operating Temperature: | 17℃ to 120℃
The contact speed of the switches shall be independent of operator speed.
4.5.11.3 Protective Devices
The transformershall be protected by a two-fuse protection system consisting of a bayonet oil-immersed,expulsion fuse in series with an oil-immersed,partial-range,current-limiting fuse.Bayonet fuse links shall sense both high currents and high oil temperature in order to provide thermal protection to the transformer. Coordinate transformer protection with expulsion fuse clearing low-current faults and current-limiting fuse clearing high-current faults beyond the interrupting rating of the expulsion fuse.In order to eliminate or minimize oil spills,the bayonet fuse assembly shall include an oil retention valve inside the housing that closes when the fuse holder is removed, and an external drip shield. The overall arrangement of the load break and protective devices shall allow loop feed to the transformer and prevent closing of the switch unto internal faults. Warning shall be displayed adjacent to the bayonet fuse cautioning against removing or inserting fuses unless the transformer has been de-energized and the tank pressure has been released as per JPS Specification # 6951-S-14 Section 4.5.11.1. The locking clips of the fuse holders,when locked in any positionshall not be damaged when closing the transformer hood. The fuse rating and manufacturer's Catalogue number of the bayonet fuse and current limiting fuse shall be identified on the combination nameplate
TESTS
5.1 | Tests defined in ANSI C57-1200 paragraph 9 shall be made in accordance with ANSI C57.12.90 by and at the expense of the manufacturer.
Production Tests
The manufacturer shall carry out standard Production Tests and,before shipment;the manufacturershall furnish certified copies of the test results for approval.No transformershall be shipped until tests results are received.Test shall include but not limited to the following:
5.1.1 | Excitation current at 100%and 110%rated voltage;test to be made with either the primary or secondary in open circuit.
5.1.2 | Winding Insulation Resistance
Losses Calculations
For the purpose of comparing Bids,the transformer losses will be evaluated on the following basis:- Evaluated cost of transformer (EC) EC = P+5.403*L1+2.412*L2 Where: EC is the evaluated cost in US$ P is CIF price of transformer in US$ Li is No Load Loss in Watts Lz is Load Loss in Watts, (On the “Transformer Data Fom”the maximum losses shall be quoted at specified voltage configuration.)